## Worksheet 1
Classification | Requirement | Recommended tests for GFM functionality
Mandatory | Voltage source behaviour | Slow-changing voltage phasor during sub-transient events (5–10 ms). The voltage should not vary sharply for any condition and must maintain a magnitude of 1 pu during the steady state.
| Synchronising active power/damping active power | Synchronising active power during the grid phase jump. The initial operating point needs to be mentioned, and the response to the phase jump begins before 5 ms.
| Inertia contribution/withstanding RoCoF | Active power response to grid RoCoF specified by the TSO. The inertial overshoot should not violate the converter's physical limits.
| Voltage support via reactive power | Reactive power response to a grid voltage dip of 5 % from nominal. The converter should follow the V–Q droop property.
| Fast-fault current contribution | Fault response should not rely on measurements. Response to faults should happen intrinsically and ideally begin before 5 ms from when the fault is applied.
| Withstand grid SCR changes | Operation at different SCR levels and SCR changes. Maximum and minimum SCR levels must be defined at the PCC for each OF WPP.
Optional | Sink for harmonics | Reject grid voltage/frequency fluctuations.
| Sink for imbalances | Ride through unbalanced faults; TSOs describe the fault severity levels. The converter operates within its hardware limitations.
| Interoperability | Time domain and frequency domain studies for a multi-GFM converter test system. Studies with black-boxed GFM WPPs with different GFM control methods are required to get a TSO perspective.
| Active power sharing/droop | Power delivery proportional to frequency change.
Advanced | Extended inertia via energy buffers | Assessed on a case-by-case basis for generation types.
| Islanding and resynchronisation | Withstand islanding and auto-resynchronisation for shorter islanding conditions. Local energy sink and resynchronisation schemes are needed to maintain stability for resynchronisation attempts followed by longer islanding.
| Surviving the loss of the last sync. gen. | Withstand sudden islanding with local loads.
| Black starting | Requires field testing.