## Worksheet
Subsystem |  | RDS-PP Code | Average failure rate onshore | Lower bound of 90 % confidence interval | Upper bound of 90 % confidence interval | Average failure rate offshore | Lower bound of 90 % confidence interval | Upper bound of 90 % confidence interval | Average rate MCR offshore | Average rate MCR JUV required | Average technicians required | Average repair time | Corrective maintenance rate (excl. failures) | Preventive maintenance rate
Unit |  |  | 1/(MWa) | 1/(MWa) | 1/(MWa) | 1/(MWa) | 1/(MWa) | 1/(MWa) | 1/(MWa) | 1/(MWa) | 1/WTvisit | h/WTvisit | 1/(MWa) | 1/(MWa)
Onshore/offshore |  |  | onshore | onshore | onshore | offshore | offshore | offshore | offshore | offshore | offshore | offshore | offshore | offshore
Environmental measuring system |  | CKJ | 0.059 | 0.0534 | 0.0652 | 0.0272 | 0.024 | 0.0307 | – | – | 2.8 | 2.6 | – | –
Rotor system incl. pitch system | Rotor system | MDA | 0.0773 | 0.0708 | 0.0843 | 0.0379 | 0.0341 | 0.042 | 0.0006 | 0.0006 | 3.2 | 4.8 | – | –
Pitch system |  | 0.3138 | 0.3006 | 0.3275 | 0.1638 | 0.1559 | 0.1721 | – | – | 3.2 | 3.3 | – | –
Drive train system |  | MDK | 0.2281 | 0.2168 | 0.2398 | 0.0921 | 0.0861 | 0.0983 | 0.0149 | 0.0097 | 2.9 | 7.6 | – | –
Yaw system |  | MDL | 0.0846 | 0.0778 | 0.0919 | 0.0784 | 0.073 | 0.0842 | - | - | 3 | 2.9 | – | –
Central hydraulic system |  | MDX | 0.0599 | 0.0542 | 0.066 | 0.0806 | 0.0751 | 0.0865 | – | – | 3.1 | 2.7 | – | –
Control system |  | MDY | 0.2548 | 0.2429 | 0.2671 | 0.1268 | 0.1198 | 0.1341 | – | – | 3.2 | 2.7 | – | –
Power generation system |  | MKA | 0.1206 | 0.1124 | 0.1292 | 0.0835 | 0.0779 | 0.0895 | 0.0209 | 0.0012 | 2.5 | 2.9 | – | –
Generator switching system |  | MSC | 0.067 | 0.061 | 0.0735 | 0.025 | 0.0219 | 0.0283 | - | - | 3.5 | 2.1 | – | –
Converter system |  | MSE | 0.2226 | 0.2115 | 0.2342 | 0.1243 | 0.1174 | 0.1315 | – | – | 3.4 | 4.2 | – | –
Generator transformer system |  | MST | 0.0252 | 0.0215 | 0.0293 | 0.0083 | 0.0066 | 0.0103 | 0.0003 | 0.0003 | 3.5 | 4.3 | – | –
Nacelle |  | MUD | 0.0267 | 0.0229 | 0.0309 | 0.0202 | 0.0175 | 0.0232 | 0 | 0 | 3.3 | 1.9 | – | –
Remote monitoring system |  | MYA | 0.0071 | 0.0053 | 0.0095 | 0.0004 | 0.0001 | 0.0011 | – | – | 2 | 2.2 | – | –
Tower system |  | UMD | 0.0204 | 0.0171 | 0.0241 | 0.0151 | 0.0128 | 0.0178 | 0 | 0 | 2.7 | 2.5 | – | –
Personnel rescue systems |  | WBA | 0.0059 | 0.0042 | 0.0081 | 0.0019 | 0.0011 | 0.003 |  | – | 2.2 | 1.4 | – | –
Fire extinguishing system |  | XGM | 0.0078 | 0.0058 | 0.0102 | 0.0041 | 0.0029 | 0.0056 | – | – | 2.9 | 2.3 | – | –
Lifting gears |  | XMM | 0.0246 | 0.021 | 0.0287 | 0.1255 | 0.1185 | 0.1327 | – | – | 2.5 | 2.8 | – | –
Obstacle warning system |  | XSD | 0.0328 | 0.0286 | 0.0374 | 0.0222 | 0.0194 | 0.0254 | – | – | 2.6 | 1.9 | – | –
Low-voltage electrical main supply system |  | BFA | 0.0006 | 0.0002 | 0.0016 | 0.0243 | 0.0213 | 0.0276 | – | – | 2.6 | 1.2 | – | –
Fire alarm system |  | CKA | 0.0044 | 0.003 | 0.0064 | 0.0155 | 0.0132 | 0.0183 | – | – | 3.4 | 3 | – | –
Transformer station |  | UAB | 0.0025 | 0.0015 | 0.0041 | – | – | – | – | – | – | – | – | –
Equipotential bonding/earthing system |  | XFB | 0.0029 | 0.0018 | 0.0046 | 0.0049 | 0.0036 | 0.0066 | - | - | 2.2 | 2.6 | – | –
Lightning protection system |  | XFC | 0.0025 | 0.0015 | 0.0041 | 0.0096 | 0.0077 | 0.0118 | – | – | 2.4 | 1.3 | – | –
Ventilation systems |  | XAM | – | – | – | 0.0029 | 0.0019 | 0.0042 | – | – | 2.2 | 1.8 | – | –
Central lubrication system |  | MDV | 0.0218 | 0.0184 | 0.0257 | 0.0015 | 0.0008 | 0.0025 | – | – | 2.5 | 1.9 | – | –
Compensation system |  | MSS | 0.0084 | 0.0063 | 0.0109 | 0.0004 | 0.0001 | 0.0011 | – | – | – | – | – | –
Common cooling system |  | MUR | 0.0078 | 0.0058 | 0.0102 | 0.0026 | 0.0017 | 0.0039 | – | – | 1.9 | 2.2 | – | –
Telephone system |  | Y | 0.0204 | 0.0171 | 0.0241 | 0.0064 | 0.0049 | 0.0082 | – | – | 2 | 0.9 | – | –
General/Other |  | G | 0.121 | 0.1128 | 0.1296 | 0.0579 | 0.0533 | 0.0629 | – | – | 3.2 | 2.6 | – | –
Wind turbine (WT) overall |  | WT | 1.7286 | 1.6973 | 1.7602 | 1.0875 | 1.0669 | 1.1084 | 0.0366 | 0.0117 | 2.8 | 2.7 | 1.6508 | 2.6637