## Worksheet 1
Service | Status | Challenge | Research and
development needs
Protection | Can provide but maybe | Restricted inverter | Different wind
| not to the extent that is | overload current | technologies' capabilities
| necessary for existing | capacity. | to provide more fault
| protection schemes. |  | current, e.g. type V
| Some wind technologies | Provision of negative- | turbines, hybrids, and
| are better than others, e.g. | sequence current during | a larger fleet of wind/solar
| DFIG. | asymmetrical faults. | plants.
Alternative protection
schemes that do not
require overload current
inverter capacity.
Specifying the fault current
behaviour of grid-forming
wind turbines when
reaching the current limit.